## Products
PRODUCT NAME | RXYSA-AV1
[5 empty] | RXYSA4A7V1B | RXYSA5A7V1B | RXYSA6A7V1B
Recommended combination |  |  |  |  | 3 x FXSA25A2VEB + 1 x FXSA32A2VEB | 4 x FXSA32A2VEB | 2 x FXSA32A2VEB + 2 x FXSA40A2VEB
Heating capacity | Nom. |  | 6°CWB | kW | 12.1 (2) | 14.0 (2) | 15.5 (2)
COP at nom. capacity | 6°CWB |  |  | kW/kW | 4.49 | 4.20 | 4.10
SCOP |  |  |  |  | 5.1 | 4.7 | 4.7
SEER |  |  |  |  | 8.2 | 7.7 | 7.6
Space cooling | A Condition (35°C - 27/19) |  | EERd |  | 3.4 | 3.1 | 3.0
|  |  | Pdc | kW | 12.1 | 14.0 | 15.5
| B Condition (30°C - 27/19) |  | EERd |  | 5.8 | 5.3 | 5.0
|  |  | Pdc | kW | 8.9 | 10.3 | 11.4
| C Condition (25°C - 27/19) |  | EERd |  | 10.9 | 9.8 | 9.8
|  |  | Pdc | kW | 5.7 | 6.6 | 7.3
| D Condition (20°C - 27/19) |  | EERd |  | 18.5 | 19.4 | 19.0
|  |  | Pdc | kW | 4.9 | 4.5 | 4.9
Space heating (Average climate) | TBivalent |  | COPd (declared COP) |  | 2.8 | 2.6 | 2.5
|  |  | Pdh (declared heating cap) | kW | 8.4 | 9.7 | 10.7
|  |  | Tbiv (bivalent temperature) | °C | -10 | -10 | -10
| TOL |  | COPd (declared COP) |  | 2.8 | 2.6 | 2.5
|  |  | Pdh (declared heating cap) | kW | 8.4 | 9.7 | 10.7
|  |  | Tol (temperature operating limit) | °C | -10 | -10 | -10
| A Condition (-7°C) |  | COPd (declared COP) |  | 3.4 | 2.9 | 2.9
|  |  | Pdh (declared heating cap) | kW | 7.4 | 8.5 | 9.5
| B Condition (2°C) |  | COPd (declared COP) |  | 4.9 | 4.5 | 4.3
|  |  | Pdh (declared heating cap) | kW | 4.5 | 5.2 | 5.8
| C Condition (7°C) |  | COPd (declared COP) |  | 7.0 | 6.7 | 7.0
|  |  | Pdh (declared heating cap) | kW | 3.3 | 3.3 | 3.7
| D Condition (12°C) |  | COPd (declared COP) |  | 8.9 | 8.9 | 9.0
|  |  | Pdh (declared heating cap) | kW | 3.9 | 3.9 | 3.9
Capacity range | HP |  |  |  | 4 | 5 | 6
Maximum number of connectable indoor units |  |  |  |  | 13 (3) | 16 (3) | 18 (3)
Indoor index connection | Min. |  |  |  | 50.0 | 62.5 | 70.0
| Nom. |  |  |  | 100 | 125 | 140
| Max. |  |  |  | 130.0 | 162.5 | 182.0
Dimensions | Unit |  | Height | mm | 869 | 869 | 869
|  |  | Width | mm | 1,100 | 1,100 | 1,100
|  |  | Depth | mm | 460 | 460 | 460
Weight | Unit |  |  | kg | 102 | 102 | 102
Fan | External static pressure |  | Max. | Pa | 45 | 45 | 45
Compressor | Type |  |  |  | Hermetically sealed swing compressor | Hermetically sealed swing compressor | Hermetically sealed swing compressor
Operation range | Cooling |  | Min. | °CDB | -5 | -5 | -5
|  |  | Max. | °CDB | 46 | 46 | 46
| Heating |  | Min. | °CWB | -20 | -20 | -20
|  |  | Max. | °CWB | 16 | 16 | 16
Sound power level | Cooling |  | Nom. | dBA | 67.0 (4) | 68.1 (4) | 69.0 (4)
Sound pressure level | Cooling |  | Nom. | dBA | 49.0 (6) | 51.0 (6) | 51.0 (6)
Refrigerant | Type |  |  |  | R-32 | R-32 | R-32
| GWP |  |  |  | 675.0 | 675.0 | 675.0
| Charge |  |  | kg | 3.40 | 3.40 | 3.40
Piping connections | Liquid |  | Type |  | Braze connection | Braze connection | Braze connection
|  |  | OD | mm | 9.52 | 9.52 | 9.52
| Gas |  | Type |  | Braze connection | Braze connection | Braze connection
|  |  | OD | mm | 15.9 | 15.9 | 15.9
| Total piping length | System | Actual | m | 300 (7) | 300 (7) | 300 (7)
| Level difference | OU - IU | Outdoor unit in highest position | m | 50 | 50 | 50
|  |  | Indoor unit in highest position | m | 40 | 40 | 40
Standard Accessories | Installation and operation manual |  |  |  | 1 | 1 | 1
| General safety precautions |  |  |  | 1 | 1 | 1
| Peel off F-gas label |  |  |  | 1 | 1 | 1
| Refrigerant label for F-gas regulation |  |  |  | 1 | 1 | 1
| Tie-wraps |  |  |  | 2 | 2 | 2
| Auxiliary piping set |  |  |  | 1 | 1 | 1
| Caution label |  |  |  | 1 | 1 | 1
Power supply | Name |  |  |  | V1 | V1 | V1
| Phase |  |  |  | 1~ | 1~ | 1~
| Frequency |  |  | Hz | 50 | 50 | 50
| Voltage |  |  | V | 220-240 | 220-240 | 220-240
Notes |  |  |  |  | (1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m | (1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m | (1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m
[5 empty] | (2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m | (2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m | (2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m
[5 empty] | (3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system. | (3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system. | (3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.
[5 empty] | (4) - Sound power level is an absolute value that a sound source generates. | (4) - Sound power level is an absolute value that a sound source generates. | (4) - Sound power level is an absolute value that a sound source generates.
[5 empty] | (5) - According to ENER Lot 21 | (5) - According to ENER Lot 21 | (5) - According to ENER Lot 21
[5 empty] | (6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings. | (6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings. | (6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.
[5 empty] | (7) - Refer to refrigerant pipe selection or installation manual | (7) - Refer to refrigerant pipe selection or installation manual | (7) - Refer to refrigerant pipe selection or installation manual
[5 empty] | (8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB | (8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB | (8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB
[5 empty] | (9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current. | (9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current. | (9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.
[5 empty] | (10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc ≥ minimum Ssc value | (10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc ≥ minimum Ssc value | (10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc ≥ minimum Ssc value
[5 empty] | (11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current. | (11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current. | (11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.
[5 empty] | (12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker). | (12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker). | (12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).
[5 empty] | (13) - TOCA means the total value of each OC set. | (13) - TOCA means the total value of each OC set. | (13) - TOCA means the total value of each OC set.
[5 empty] | (14) - FLA means the nominal running current of the fan | (14) - FLA means the nominal running current of the fan | (14) - FLA means the nominal running current of the fan